## b504
B5h 04h - Get Data Block

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 04h	Get Date/Time
M5	NN = 01h	Length of data
M6	00h	Data Block Identifer
M7	CRC
S1	ACK
S2	NN = 0Ah	Length of data
...

Block 00h - Date/Time

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 04h	Get Data Block
M5	NN = 01h	Length of data
M6	DB = 00h	Block 00h (Date/Time)
M7	CRC
S1	ACK
S2	NN = 0Ah	Length of data
S3		DCF77 status:			BYTE
	00h
	01h	no receiption
	02h	receiption
	03h	synchronized
		data valid
S4	ss	Seconds	Sec	0..59	BCD
S5	min	Minutes	Min	0..59	BCD
S6	hh	Hours	Hour	0..59	BCD
S7	dd	Day		1..31	BCD
S8	mm	Month		1..12	BCD
S9	ww	Weekday		1..7	BCD
S10	yy	Year		0..99	BCD
S11	TA_L	Outside temperature	°C	-50,0 – 50,0	DATA2b [1/256]
S12	TA_H
S13	CRC
M8	ACK
M9	SYN

Block 01h - Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					26h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 01h	Block 01h					01h
M7	CRC					D8h
S1	ACK					00h
S2	NN = 09h	Length of data					09h
S3	tt	set temperature	°C		char		14h

		- room: ZZ=26h

		- service water: ZZ=25h
S4					04h, 03h
S5					00h
S6					00h
S7					02h
S8					05h
S9					00h
S10	dd	night=0 / day=1	On/Off		char		00h
S11					00h
S12	CRC					2Ch
M8	ACK					00h
M9	SYN					AAh

Block 02h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					26h/25h/23h

		HK1: 26h; WW:25h; ZP:23h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 02h	Block 02h					02h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 07h	Length of data					07h
S3	TB1	Zeitfenster1 Beginn	10Min		char
S4	TE1	Zeitfenster1 Ende	10Min		char
S5	TB2	Zeitfenster2 Beginn	10Min		char
S6	TE2	Zeitfenster2 Ende	10Min		char
S7	TB3	Zeitfenster3 Beginn	10Min		char
S8	TE3	Zeitfenster3 Ende	10Min		char		03h
S9	DAY				char
S9	CRC					B2h
M8	ACK					00h
M9	SYN					AAh

Block 09h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h 10h
M2	ZZ	Target address					23h 25h 26 50 EC
M3	PB = B5h	Vaillant command					B5h B5h
M4	SB = 04h	Get Data Block					04h 04h
M5	NN = 01h	Length of data					01h 01h
M6	DB = 09h	Block 09h					09h 09h
M7	CRC					CEh DAh
S1	ACK					00h 00h
S2	NN = 0Ah	Length of data					0Ah 0Ah
S3		RaumTemp			char		14h 37h
S4		AbsenkTemp			char		00h 00h
S5		Heizkurve * 10			char		00h 00h
S6					00h 00h
S7					06h 03h
S8		AT-AbschaltTemp			char		16h 16h
S9					00h 00h
S10		MinTempVL			char		0Fh 0Fh
S11		MaxTempVL			char		4Bh 5Ah
S12					00h 00h
S13	CRC					80h 4Eh
M8	ACK					00h 00h
M9	SYN					AAh AAh

Block 0Dh– service water

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					23h 25h 26 50 EC
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 0Dh	Block 0Dh					0Dh
M7	CRC					CAh
S1	ACK					00h
S2	NN = 05h	Length of data					05h
S3	VL_TT	flow set temperature	°C		char		00h
S4
S5	TT_L	Temperature of the service water store (ZZ=25h)	°C		DATA2c		00h
S6	TT_H
		Tempeature of flow water (Z=26h)
S7	R_TT	room set temperature	°C		char		00h

		ZZ=26h
S8	CRC					4Ch
M8	ACK					00h
M9	SYN					AAh

Block 0Fh – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 0Fh	Block 0Fh					0Fh
M7	CRC					C7h
S1	ACK					00h
S2	NN = 0Ah	Length of data					0Ah
S3	XX = 14h					59h
S4	XX = 00h					03h
S5	XX = 00h					3Ch
S6	XX = 00h					03h
S7	XX = 06h					21h
S8	XX = 16h					FFh
S9	XX = 00h					21h
S10	XX = 0Fh					FFh
S11	XX = 4Bh					00h
S12	XX = 00h					00h
S13	CRC					E4h
M8	ACK					00h
M9	SYN					AAh

Block 10h – Temperatur Waterstorage

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 10h	Block 10h					10h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 0Ah	Length of data					0Ah
S3	TW1_L	Service-Water Temperatur 1	°C		DATA2C		50h
S4	TW1_H					0Ch
S5	TW2_L	Service-Water Temperatur 2	°C		DATA2C		08h
S6	TW2_H					50h
S7	TW3_L	Service-Water Temperatur 3	°C		DATA2C		07h
S8	TW3_H					03h
S9	TD1_L	Tempeartursensor TD1	°C		DAT2C
S10	TD1_H
S11	TD2_L	Tempeartursensor TD1	°C		DATA2C
S12	TD2_H
S10	CRC					B2h
M8	ACK					00h
M9	SYN					AAh

Block 11h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 11h	Block 11h					11h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 06h	Length of data					06h
S3					50h
S4					0Ch
S5					08h
S6					50h
S7					07h
S8					03h
S9	CRC					B2h
M8	ACK					00h
M9	SYN					AAh

Block 12h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 12h	Block 12h					12h
M7	CRC					DAh
S1	ACK					00h
S2	NN = 0Ah	Length of data					0Ah
S3					4Bh
S4					00h
S5					00h
S6					67h
S7					0Bh
S8					00h
S9					80h
S10					00h
S11					00h
S12					00h
S13	CRC					0Bh
M8	ACK					00h
M9	SYN					AAh

Block 17h – Service Water day time

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					25h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 17h	Block 17h					17h
M7	CRC					DAh
S1	ACK					00h
S2	NN = 01h	Length of data					0Ah
S3	AA	Service time for Service water	OnOff		char
S4	CRC
M8	ACK					00h
M9	SYN					AAh

Block 18h – Heating-Lead-Temperature for HK2 (Mixer) incl. Raising-Temp.
(Kessel-Soll für HK2 incl. Temperaturüberhöhung )

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					50h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 17h	Block 17h					18h
M7	CRC					E7h
S1	ACK					00h
S2	NN = 01h	Length of data					06h
S3	HLT_KH2_L	Heizkessel-Solltemperatur für Versorgung HK2 mit Offset "Temperaturüberhöhung"			data2b		20h
S4	HLT_HK2_H					1fh
S5		unknown - always 00h					00h
S6	HK2_T_L	Vorlauftemperatur HK2			data2c		9dh
S7	HK2_T_H					01h
S8		unknown					15h or 13h
S9	CRC					86h
M8	ACK					00h
M9	SYN					AAh

Block 21h – Service water storage

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 11h	Block 11h					11h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 05h	Length of data					05h
S3	CC	Collector temperature	°C		char
S4	DD	unkown					00h
S5	EE	heater source			char
		0: off
		1: solar
		2: heater
S6	FF	Storage level	%		char		Entspricht der Füllstandsanzeige im IDLE-Display der Steuerung
S7	GG	Power	%		char		Entpsricht Balken- anzeige im Display
S8	CRC
M8	ACK					00h
M9	SYN					AAh

Block 22h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 12h	Block 11h					11h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 03h	Length of data					05h
S3	OO	unkown					00h
S4	PP	unkown					04h
S5	QQ	unkown					07h
S6	CRC					24h
M8	ACK					00h
M9	SYN					AAh

Block 25h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 25h	Block 25h					25h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 02h	Length of data					02h
S3	PP	unknown					07h
S4	QQ	unkown					03h
S5	CRC					D8h
M8	ACK					00h
M9	SYN					AAh

Block 26h – VR 81 remote control unit for VRC 430(f)/470(f)

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ = 30h	Source address
M2	ZZ = 26h	Target address
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 26h	Block 26h					26h
M7	CRC
S1	ACK
S2	NN = 07h	Length of data
S3	?
S4	MO	Current mode of operation:			byte
		00h=heating disabled, 02h=day, 03h=day, 04h=night
S5	?
S6	RS	Target room temperature	°C		data1c
S7	?
S8	RC_L	Current room temperature (corrected by offset value)	°C		data2c
S9	RC_H
S10	CRC
M8	ACK					00h
M9	SYN					AAh

The current room temperature in this frame (bytes S8 and S9, RC_L and RC_H) is unreliable and should not be used! Instead, use the data from the frame (qq=30h, zz=26h, pb=B5h, sb=05h, nn=05h, first data byte 3Ch).
Also note that the byte S6 has been found to be missing if the target room temperature is set to 22.0°C. It is unclear whether this is intentional or a bug.

Block 28h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 28h	Block 28h					28h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 03h	Length of data					05h
S3	SE_L	Solarertrag	kWh		word
S4	PP
S5	QQ	unkown					00h
S6	CRC					24h
M8	ACK					00h
M9	SYN					AAh

Block 36h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					ECh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 04h	Get Data Block					04h
M5	NN = 01h	Length of data					01h
M6	DB = 36h	Block 36h					36h
M7	CRC					D9h
S1	ACK					00h
S2	NN = 01h	Length of data					01h
S3	QQ	unkown					00h
S4	CRC					9Bh
M8	ACK					00h
M9	SYN					AAh

## b505
B5h 05h – Burner Operational Data

This Broadcast informs about the operational data of the burner control unit. It seems to be a Vaillant specific variant of Service 08h 01h.
This frame can be used to determine the current room temperature reliably. The target room temperature and the current heating status (off, day, night) can be found in the frame (qq=30h, zz=26h, pb=B5h, sb=04, nn=01, first data byte 26h).
Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ = FEh	Target address
M3	PB = B5h	Vaillant command
M4	SB = 05h	Burner Operational Data?
M5	NN = 02h	Length of data
M6	xx = 04h					unknown

	xx = 29h
M7	yy = 00h					unknown
M8	CRC
M9	SYN
Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					VRS620
M2	ZZ = FEh	Target address
M3	PB = B5h	Vaillant command
M4	SB = 05h	Burner Operational Data
M5	NN = 04h	Length of data
M6	xx = 27h	(unknown)					unknown
M7		Bit0 = BW_load			BYTE		00h, 01h

					This bit is active when service water is loaded.
M8	VT	Lead water temperature	°C	0-89	CHAR	5A h	Vorlauftemperatur IST HK1

					VF1-Fühler
M9		Bit0 = BW_load			BYTE		00h, 01h

					This bit seems to be synchronous to M7 Bit0.
M10	CRC
M11	SYN

.M6 xx=2Dh gesehen, dabei haben die Daten M7 - M9 aber andere Werte gehabt.

Block 36h – Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					FEh
M3	PB = B5h	Vaillant command					B5h
M4	SB = 05h	Get Data Block					04h
M5	NN = 02h	Length of data					01h
M6	DB = 06h	Block 06h					06h
M7	NN	On/OFF??					Zubegin von Einmaliger Speicherladung mit 01h und zum Ende 00h

					00h / 01h
M8	CRC					D9h

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					VRS620
M2	ZZ = FEh	Target address
M3	PB = B5h	Vaillant command
M4	SB = 05h	Burner Operational Data
M5	NN = 08h	Length of data
M6	xx = 2Bh	(unknown)					unknown
M7					gesehen 0Fh
M8					gesehen 01h
M9					gesehen 00h
M10					gesehen 00h
M11					gesehen 00h
M12					gesehen 00h
M13					gesehen 80h
M14	CRC
M15	SYN

Block 3C - VR 81 remote control unit for VRC 430(f)/470(f)

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ = 30h	Source address					30h
M2	ZZ = 26h	Target address					26h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 05h	Get Data Block					05h
M5	NN = 05h	Length of data					05h
M6	DB = 3Ch	Block 3Ch					3Ch
M7	RC_A_L	Current room temperature (not corrected by offset value)			data2c
M8	RC_A_H
M9	RC_B_L	Current room temperature (corrected by offset value)			data2c
M10	RC_B_H
M11	CRC					D9h
M12	ACK

## b506
B5h 06h - Unknown Broadcast 2

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ = FEh	Target address					Broadcast
M3	PB = B5h	Vaillant command
M4	SB = 06h	Unknown broadcast 2
M5	NN = 02h	Length of data
M6	xx = 00h					unknown
M7	yy = 00h					unknown
M8	CRC
M9	SYN
Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ = FEh	Target address					Broadcast
M3	PB = B5h	Vaillant command
M4	SB = 06h	Unknown broadcast 2
M5	NN = 01h	Length of data
M6	xx = 01h					unknown
M7	CRC
M8	SYN

## b509
B5h 09h - Get or Set Device Configuration or Status (Get Solar Data)

The Get Device Configuration or Status command is used for requesting specific data from other eBus devices. It is used by vrDialog software to read and display device configuration and status data on the screen, or set device parameters. Each device has a number of parameters that can be read or set using this command.

Block 0Dh - Read device configuration or status parameters

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address					ECh, 10h (room controller), 15h (burner)
M3	PB = B5h	Vaillant command
M4	SB = 09h	Get or Set Device Configuration or Status
M5	NN = 03h	Length of data
M6	DB = 0Dh	Block 0Dh: Read device configuration or parameters
M7	P1 = xx1h	Low byte of parameter address					For Solar devices:
			°C
		Sensor:	°C
		00h: water basin 1]	°C				SP1
		01h: water basin 2	°C				SP2
		02h: water basin 3	°C				SP3
		03h: Collector 1	°C				Kol1
		04h: Collector 2					Kol2 / VF1[1]
		05h: Gain					Ertrag

					For other devices there are different address values (see below)
M8	P2 = xx2h	High byte of parameter address					High byte of parameter address

		Parameter 2
M9	CRC
S1	ACK
S2	NN = 03h	Length of data					Response depends on requested parameter type (see below)
S3	D_L	Sensor Value			DATA2c
S4	D_H
					[1/16]
S5	00h	sensor connected			CHAR
	AAH	no sensor connected
S6	CRC
M10	ACK
M11	SYN

[1] auroMATIC 620

The 0Dh command seems to be implemented by all Vaillant eBus devices. vrDialog application includes a file vrDIALOG810.mdb, that contains MS Access database used internally by vrDialog. This database can be accessed in order to read different configuration parameters for different supported types of Vaillant eBus devices. For example, using this database for VRT360, it the following command can be executed:

select SymList .name, type, address from ShowData , SymList where ShowData .page ='VRT360' and SymList .id = ShowData .varid and accesslevel < 50 order by ShowData .sortid=

This results in:

Name	Type	Address
RaumtemperaturIst	Temperatursensor	15
ActualRoomTempSetpoint	TIte	87
StatusDcf	DcfState	38
IsInQuickVeto	OnOff	49
QuickVetoTemp	TIte	50
IsInSavingsFunction	OnOff	44
SavingsFunctionTime	SaveFunction	45
IsInParty	OnOff	41
IsInSingleDHWLoadingMode	OnOff	42
IsInHoliday	uchar	40

The Address column needs to be passed as P1 and P2 parameters to the 0Dh command. The Type column determines the type of the response from the device. The response length will depend on that (S2 byte in the response).

Here is a captured communication between vrDialog and VRT360:

FF 15 B5 09 03 0D 0F 00 67 00 03 57 01 00 3A 00

FF - vrDialog Master address (vrDialog identifies itself as FFh)

15 - VR360 slave address

B5 09 - Vaillant command B509

03 - data length

0D - command 0Dh

0F - requested address low byte (0F -> 15 in the table above, which means "RaumtemperaturIst" - actual room temperature)

00 - requested address high byte

67 - CRC

00 - slave ACK

03 - slave response length - 3 bytes

57 - response temperature low byte

01 - response temperature high byte. Actual reported temperature is 157h/16 -> 21.43 Celsius

00 - temperature sensor status - 00h - OK. According to vrDialog810.mdb, sensor status is defined as follows: "struct {Data2c Temperature; State SensorState } Sensor state is defined : State "Ok,Short circuit=85,cutoff=170"

Block 0Eh - Set device configuration

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address					ECh, 10h (room controller), 15h (burner)
M3	PB = B5h	Vaillant command
M4	SB = 09h	Get or Set Device Configuration or Status
M5	NN = XXh	Length of data, variable depends on type of parameter that is being set
M6	DB = 0Eh	Block 0Eh: Set device configuration
M7	P1 = xx1h	Low byte of parameter address					This is low byte of parameter address. It is set in the same way as command 0Dh (above)
M8	P2 = xx2h	High byte of parameter address					High byte of parameter address

		Parameter 2
M9...MXX		Data that is being written as device parameter. The length of the data depends on type of variable being modified. The length is the same as the length of data returned from 0Dh command (see above)
MXX+1	CRC
S1	ACK
S2	00h - length
S3	CRC
MXX+2	ACK
MXX+3	SYN

This command works in a similar way as 0Dh, but instead of returning configuration from the device, it sets device configuration.

Block 18h - Unknown

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address					10h
M2	ZZ	Target address					26h
M3	PB = B5h	Vaillant command					B5h
M4	SB = 09h	Get Solar Data Block					09h
M5	NN = 01h	Length of data					01h
M6	DB = 18h	Block 18h					18h
M7	CRC					3Fh
S1	ACK					00h
S2	NN = 0Ah	Length of data					0Ah
S3					00h
S4					00h
S5					00h
S6					00h
S7					00h
S8					00h
S9					00h
S10					00h
S11					00h
S12					00h
S13	CRC					9Fh
M8	ACK

## b510
B5h 10h - Operational Data from Room Controller to Burner Control Unit

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 10h	Operational Data from Room Controller to Burner Control Unit
M5	NN = 09h	Length of data
M6	xx1					unknown, always 00h
M7	xx2					unknown, always 00h
M8	LT	Lead water target temperature	°C	0 – 100	DATA1c
		(Vorlauftemperatur)
M9	ST	Service water target temperature	°C	0 – 100	DATA1c
M10	xx3					unknown, always FFh
M11	xx4					unknown, always FFh
M12	xx5 = 00h				Bits:		combination of bit values. Each bit means to turn off specific feature, like service water heating. This is used by the room controller to stop the boler from heating (when the temperature is enough), or stop service water heating

	#NAME?				01 - if set, means to TURN OFF heating
	#NAME?
	#NAME?				04 - if set means to TURN OFF service water heating
	#NAME?
	#NAME?				40 - unknown?
	#NAME?
	#NAME?
M13	xx6					unknown, always FFh
M14	xx7					unknown, always 00h
M15	CRC
S1	ACK
S2	NN = 01h	Length of data
S3	zz = 01h	(acknowledge ?)					unknown
S4	CRC
M16	ACK
M17	SYN

## b511
B5h 11h 01h - Operational Data of Burner Control Unit to Room Control Unit

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 11h	Operational Data
M5	NN = 01h	Length of data
M6	01h	Block number
M7	CRC
S1	ACK
S2	NN = 09h	Length of data
S3	VT	Lead water temperature (Vorlauf-/ Anlagentemperatur)	°C	0 – 100	DATA1c
S4	NT	Return water temperature (Nachlauftemperatur)	°C	0 – 100	DATA1c
S5	TA_L	Outside temperature	°C	-50,0 – 50,0	DATA2b [1/256]
S6	TA_H
S7	WT	(WW-Auslauftemperatur)	°C	0 – 100	DATA1c
S8	ST	Service water temperature (WW-Speichertemperatur)	°C	0 – 100	DATA1c
S9	vv	Bit 0: Heating			BIT		0 = OFF
		Bit 1: Service Water
					1 = ON
S10	xx1					unknown, always 00h
S11	xx2					unknown, always FFh
S12	CRC
M8	ACK
M9	SYN

B5h 11h 02h - Operational Data of Burner Control Unit to Room Control Unit

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 11h	Operational Data
M5	NN = 01h	Length of data
M6	02h	Block number
M7	CRC
S1	ACK
S2	NN = 05h	Length of data
S3	xx1					unknown, always 03h
S4	xx2					unknown, always 3Ch
S5	xx3					unknown, always 96h
S6	xx4					unknown, always 46h
S7	ST	Service water target temperature	°C	0 – 100	DATA1c
S8	CRC
M8	ACK
M9	SYN

## b512
B5h 12h - Unknown Command

Date/Time:

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ	Target address
M3	PB = B5h	Vaillant command
M4	SB = 12h	Unknown command [ping ?]
M5	NN = 02h	Length of data
M6	xx	?
M7	yy	?
M8	CRC
S1	ACK
S2	NN = 00h	Length of data
S3	CRC
M9	ACK
M10	SYN

The following cases were observed:

Heater Controller (Master 10h) → Firing Automat 1 (Slave 08h):
(xx = 00h, yy = 00h) hot water circulating pump is off
(xx = 00h, yy = 64h) hot water circulating pump is on

Firing Automat 1 (Master 03h) → Pump 1 (Slave 64h):
(xx = 02h, yy = 00h) internal pump is off
(xx = 02h, yy = 64h) internal pump is on and operating in the service water circuit
(xx = 02h, yy = FEh) internal pump is on and operating in the heating circuit
(xx = 03h, yy = 00h) internal pump is disabled due to error condition (such as water pressure too low)

Firing Automat 1 (Master 03h) → PC/ Modem (Slave 05h):
(xx = 03h, yy = 00h)

## b516
B5h 16h 00h - Broadcast Service

Date/Time:

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ = FEh	Target address					Broadcast
M3	PB = B5h	Vaillant command
M4	SB = 16h	Broadcast Service
M5	NN = 08h	Length of data
M6	00h	Broadcast Date/Time
M7	ss	Seconds	Sec	0..59	BCD
M8	min	Minutes	Min	0..59	BCD
M9	hh	Hours	Hour	0..59	BCD
M10	dd	Day		1..31	BCD
M11	mm	Month		1..12	BCD
M12	ww	Weekday		1..7	BCD
M13	yy	Year		0..99	BCD
M14	CRC
M15	SYN

B5h 16h 01h - Broadcast Service

Outside Temperature:

Master/ Slave Byte-No.	Abbrev.	Description	Unit	Range	Type/ [Res.]	Repl. Value	Note
M1	QQ	Source address
M2	ZZ = FEh	Target address					Broadcast
M3	PB = B5h	Vaillant command
M4	SB = 16h	Broadcast Service
M5	NN = 03h	Length of data
M6	01h	Broadcast outside temperature
M7	TA_L	Outside temperature	°C	-50,0 – 50,0	DATA2b [1/256]
M8	TA_H
M14	CRC
M15	SYN